| SPECIFITION FOR BURIED PE PIPE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A | July.18.‘12 | For Approval | M.H.K | D.H.L | M.H.K |
| REV. | DATE | DESCRIPTION | DSGN | CHKD | APPD |
| OWNER : ENH-KOGAS SA |  |  |  |  |  |
| PURCHASER : KOGAS MOZAMBIQUE LDA |  |  |  |  |  |
| PROJECT : MAPUTO NATURAL GAS DISTRIBUTION PROJECT |  |  |  |  |  |
| ENGINEER : N/A - |  |  |  |  |  |

# CONTENTS

1.0	SCOPE	1

2.0	DEFINITIONS	1

3.0	CODES AND STANDARD	1

4.0	GENERAL REQUIREMENTS	1

5.0	DESIGN CRITERIA	2

6.0	MATERIAL REQUIREMENTS	3

7.0	TEST AND INSPECTION	5

8.0	MARKING	7

9.0	PACKING, TRANSPORTATION AND STORAGE	7

10.0	QUALITY ASSURANCE AND GURANTEES	7

11.0	DRAWING AND DOCUMENTATION REQUIREMENT	8

# ATTACHMENTS

Ⅰ	INSPECTION REQUIREMENTS

Ⅱ	VENDOR DATA REQUIREMENTS

Ⅲ	BILL OF QUANTITY

1.0	SCOPE

# This specification covers the minimum technical and associated requirements for manufacturing and supply of buried polyethylene(PE) pipe and fitting for Maputo Natural Gas Distribution Project, in the Republic of Mozambique.

# VENDOR shall be responsible for, but not be limited to, the supply of materials, fabrication, shop inspection and tests, mechanical and performance guarantee, packing and transportation.

2.0	DEFINITIONS

# The following definitions shall be applied to the standard terms used throughout this document.

# PACHASER : KOGAS MOZAMBIQUE LDA

# VENDOR : Manufacture and / or Supplier

# PE Pipe : Polyethylene pipe

3.0	CODES AND STANDARDS

# The pipes and fittings shall be manufactured, inspected and tested in accordance with, but not limited to, the latest edition of the following codes and standards:

# - ISO 4437 : Buried polyethylene (PE) pipes for the supply of gaseous fuels

# - ISO 8085-1 : Polyethylene fittings for use with polyethylene pipes for the supply of gaseous

# fuels - Part 1: Fittings for socket fusion using heated tools

# - ISO 8085-2 : Polyethylene fittings for use with polyethylene pipes for the supply of gaseous
fuels - Part 2: Spigot fittings for butt fusion, for socket fusion using heated tools and for use with electro fusion fittings

# - ISO 8085-3 : Polyethylene fittings for use with polyethylene pipes for the supply of gaseous

# fuels - Metric series - Specifications - Part 3: Electro fusion fittings

# - ISO 10933 : Polyethylene (PE) valves for gas distribution systems

# - ISO 11357 : Plastics – Differential Scanning Calorimetry (DSC) – Part 6: Determination of
Oxidation Induction Time.

4.0	GENERAL REQUIREMENTS

# 4.1	The materials shall be supplied in accordance with “ Bill of Quantity sheets” herein attached.

# 4.2	All materials shall be new, clean free from rust, pits and defects.

# 4.3	The diameter and thickness of PE pipe shall be in accordance with ISO 4437, unless otherwise specified.

5.0   DESIGN CRITERIA

5.1   Natural Gas Composition

| Components | Unit Molecular Weight (kg/kg-mol) | Composition (mol %) | Molecular Weight (kg/kg-mol) |
| --- | --- | --- | --- |
| CH4 | 16.0429 | 94.20297 | 15.11 |
| C2H6 | 30.0699 | 2.11619 | 0.64 |
| C3H8 | 44.0970 | 0.88491 | 0.39 |
| n-C4H10 | 58.1240 | 0.26004 | 0.15 |
| i-C4H10 | 58.1240 | 0.22030 | 0.13 |
| n-C5H12 | 72.1510 | 0.05578 | 0.04 |
| i-C5H12 | 72.1510 | 0.06877 | 0.05 |
| C6H14 | 86.1779 | 0.09636 | 0.08 |
| C7H16 | 100.205 | 0.04270 | 0.04 |
| C8+ | 114.232 | 0.01128 | 0.01 |
| N2 | 28.0130 | 2.04070 | 0.57 |
| Total | - | 100 | 17.22 |

- NG Components(@15℃, 1atm)`

5.2   Piping rating shall be classified in accordance with gas supply pressure as follows.

| Line Class | Pressure (MPa) |  | Rating (ANSI Class) | Material |
| --- | --- | --- | --- | --- |
|  | Design Pressure | Operating Pressure |  |  |
| P7 | 7.55 | 6.86 | 600# | API 5L Gr.X60 API 5L Gr.X42 |
| P2 | 2.16 | 1.96 | 300# | API 5L Gr.A, ASTM A53 Gr.A |
| P0.4 | 0.43 | 0.39 | 150# | HDPE |

# 5.3   Design Temperature : 0℃ ~ +60℃

6.0	MATERIAL REQUIREMENTS

# 6.1	Raw material properties

# 6.1.1  Density and composition

# The base material of the pipe and fitting shall be of density not less than 930 ㎏/㎥ to which shall be added only those anti-oxidants, UV stabilizers and yellow master batch, necessary for the manufacture of pipe.

# 6.1.2  Melt Flow Index

# To facilitate extruding, the manufacturer shall be quote the melt flow index of the PE pipe, determined in accordance with ISO 1133.

# The melt flow index of pipes to be extruded shall not differ more than 0.4g/10min.

# 6.1.3  Pigment dispersion

# The colour master batch content shall be ≤ 3 grade.

# 6.1.4  Oxidative induction time

# Oxidative induction time is determined in accordance with ISO 11357-6

# Determination of oxidation induction time or OIT is the primary means of finding out the resistance of polyethylene pipes to oxidation. OIT is determined using a differential thermal analysis (DTA) instrument. The procedure essentially subjects the pipe to an accelerated oxidation environment, while monitoring for the occurrence of exothermic and endothermic reactions. Thus, the longer the OIT, the more oxidation resistant the pipe is. A useful comparison would be to find out the OIT of the unprocessed resin and the OIT of the processed plastic. The discrepancy between the OIT’s of the two basically reveals the extent of the impact of polymer processing on the reduction of oxidation resistance.

# 6.1.5  Volatile content

# Volatile content is determined in accordance with ISO 12099

# Specifies a method for determining the content of material volatile at 105 °C in polyethylene (PE) piping materials. This method is applicable to moulding and extrusion materials. It also can be applicable to components in PE piping systems.

# 6.1.6  Water absorption

# This International Standard specifies a method for the determination of moisture content in thermoplastics. This method is only applicable to thermoplastics for which the melting point

# is below 160 °C. The method is suitable for measuring the moisture content down to 0,0005 %. This method determines the total moisture content in the test piece and included surface moisture and moisture contained within the test piece. Because the test piece is converted to a molten state, it is assumed that all moisture is expelled.

# 6.1.7  Resistance to gas constituents

# Compounds complying with this Standard are not intended for use with gas containing more than 1% aromatics by volume. Where aromatic content is greater than this, testing for resistance to gas constituents should be carried out in accordance with ISO 4437.

# 6.1.8  Resistance to rapid crack propagation.

# The resistance of a polyethylene pipe material to rapid crack propagation (RCP) is measured according to ISO 13477. A large diameter pipe section is pre-cracked at one

# end, chilled to 0℃, placed under internal pressure, and then the pre-crack is impacted with a chisel propelled at 20m/s.

# 6.1.9  Resistance to slow crack growth.

# The resistance of a polyethylene pipe material to slow crack growth is measured according to ISO 13479. This test is similar to the internal pressure creep rupture test, except that the test pieces are deliberately notched before testing. Four longitudinal notches, offset by 90°, are machined into the test piece. Each notch is a 60° chevron notch with a depth equal to 20% of the wall thickness.

# 6.2	Pipe properties

# 6.2.1  Dimensions

# The dimensions of the pipes shall be measured not less than 24h after manufacture in accordance with ISO3126 after being conditioned for at least 4h.

# The mean outside diameter and the out-of-roundness(ovality) and their tolerances shall conform to ISO 4437.

# For close-tolerance pipes Grade B tolerance shall apply, and for other pipes Grade A tolerance, where these tolerance grades shall conform to ISO 11922/1

# 6.2.2  Elongation at break

# Elongation at break shall be in accordance with ISO6259-1.

# The ability of a material to resist breaking under tensile stress is one of the most important and widely measured properties of materials used in structural applications. The force per unit area (MPa or psi) required to break a material in such a manner is the ultimate tensile strength or tensile strength at break.

# 6.2.3  Heat reversion

# The longitudinal length at any position on the pipe shall not change be more than 3%. On inspection after testing, the pipe shall not show any faults, cracks, cavities, or blisters.

# 6.2.4  Melt Flow Index

# To facilitate extruding, the manufacturer shall be quote the MFI of the PE pipe, determined in accordance with ISO 1133.

# The melt flow index of pipes to be extruded shall not differ more than 0.4g/10min.

# 6.2.5  Weathering resistance

# Resistance to weathering is determined in accordance with the procedure established in ISO 4437 Annex C.

# The yellow material for gas pipes contains suitable light stabilizers. These ensure resistance to the ultraviolet rays of sunlight for an outdoor storage.

# 6.2.6  Resistance to rapid crack propagation.

# The resistance of a polyethylene pipe material to rapid crack propagation (RCP) is measured according to ISO 13477. A large diameter pipe section is pre-cracked at one end, chilled to 0℃, placed under internal pressure, and then the pre-crack is impacted with a chisel propelled at 20m/s.

# 6.2.7  Resistance to slow crack growth.

# The resistance of a polyethylene pipe material to slow crack growth is measured according to ISO 13479. This test is similar to the internal pressure creep rupture test, except that the test pieces are deliberately notched before testing. Four longitudinal notches, offset by 90°, are machined into the test piece. Each notch is a 60°chevron notch with a depth equal to 20% of the wall thickness.

# 6.2.8  Oxidative induction time

# Oxidative induction time is determined in accordance with ISO 11357-6

# Determination of oxidation induction time or OIT is the primary means of finding out the resistance of polyethylene pipes to oxidation. OIT is determined using a differential thermal analysis (DTA) instrument. The procedure essentially subjects the pipe to an accelerated

# oxidation environment, while monitoring for the occurrence of exothermic and endothermic reactions. Thus, the longer the OIT, the more oxidation resistant the pipe is. A useful comparison would be to find out the OIT of the unprocessed resin and the OIT of the processed plastic. The discrepancy between the OIT’s of the two basically reveals the extent of the impact of polymer processing on the reduction of oxidation resistance.

# 6.2.9  Hydrostatics strength

# The ISO 1167 specifies a method for determining the resistance of thermoplastics pipes to constant internal gas pressure at constant temperature. This standard applies to thermoplastics pipes intended for the transport of fluids.

| PIPE & FITTING MATERIAL | Test stress(MPa) |  |  |
| --- | --- | --- | --- |
|  | 100h at 20℃ | 165h at 80℃ | 1,000h at 80℃ |
| PE100 | 12.4 | 5.5 | 5.0 |

7.0	TEST AND INSPECTION

# 7.1	PE pipe do not erode/corrode or develop scales, and their resistance to acid and alkaline renders them perfect for supplying natural gas

# 7.2	Mechanical properties

| Item |  | Unit | Standard of Quality | Condition | Method |
| --- | --- | --- | --- | --- | --- |
| Internal Pressure Creep |  | time | Break-up time ≥ 100 | 20℃ PE100 9.0MPa12.4MPa | ISO 1167 |
|  |  |  | Break-up time ≥ 165 | 80℃ PE 100 4.6MPa 5.5MPa 4.0MPa 5.0MPa |  |
|  |  |  | Break-up time ≥ 1,000 |  |  |
| Elongation at Break |  | % | ≥350 | - | ISO 6259-3 |
| Weather ability (Except Black pipe) |  | - | After weathering the requirements for thermal stability, HS(165h/80℃) and elongation at break shall be met. | E≥3.5GJ/m | ISO 1167 ISO 6259-3 ISO/TR 10837 |
| (RCP) | Full Scale Test (dn≥250mm) | Mpa | Critical Pressure≥MOP×1.5 | 0℃ | ISO 13478 |
|  | S4Test (en≥15mm) | Mpa | Critical Pressure≥ MOP/2.4-0.072 | 0℃ | ISO 13477 |
| Slow Crack Growth(SCG) (en≥5mm) |  | Hr | 165 | 80℃,0.8MPa 80℃,0.92MPa | ISO 13479 |
| Density |  | kg/㎥ | ≥930 | 23℃ | ISO 1183 ISO 1872-1 |
| Heat Stability |  | min | 〉20 | 200℃ | ISO/TR 10837 |
| Melt Flow Index |  | g/10min | 1) Change in MFR by processing<20% 2) ±30% of the value nominated by the pipe manufacturer | 190℃ | ISO 4440-1 |
| Flexible Heating |  | % | ≤, no effect on surface | 110℃ | ISO 2505-1,-2 |

# 7.3	All inspection, examinations, tests, and workmanship of individual pipe material shall comply with the requirements of the applicable codes and standards.

# 7.4	Test report and certificates resulting from the tests shall be submitted to PURCHASER for approval, according to the ‘INSPECTION REQUIREMENTS’ herein attached.

8.0	MARKING

# 8.1	The pipe and fitting shall be marked by any suitable method which does not affect the functional properties of the pipes and fitting and which is able to withstand condition of handling, storage and use.

# 8.2	The manufacturer of the pipe and fitting shall mark thereon;

# - Raw material of the PE, by code.

# - Nominal diameter and nominal wall thickness of the gas pipe and fitting.

# - Year and week of manufacture (possibly by code).

# - Manufacturer's identification.

9.0	PACKING, TRANSPORTATION AND STORAGE

# 9.1	Pipes shall be covered with protectors and vinyl sheets to prevent any damage and any ingress of foreign materials into the pipes.

# 9.2	Pipes shall be transported after solidly being packed on wooden skids and with protection structures.

# 9.3	All materials are to be handled with proper equipment and in a careful manner to prevent distortion or damage.

# 9.4	All items shall be prepared for shipment in such a manner to avoid damage of atmospheric corrosion to inside or outside surface during storage period and while in transit.

10.0	QUALITY ASSURANCE AND GURANTEES

# 10.1	VENDOR shall have a quality assurance program to verify that items and services are complying with the purchaser order requirements and service.

# 10.2	All manufacturing, test and inspection defined in the purchaser order may be subject to quality assurance surveillance by purchase or his representative.

# 10.3	VENDOR shall work as per Quality Assurance Program approved by PURCHASER. VENDOR shall submit a controlled copy of the approved Quality Assurance Manual for PURCHASER’s permission to proceed.

# 10.4	VENDOR shall control the quality of items and services to meet the requirements of this specification, applicable code and standards, and other contract documents.

# 10.5	VENDOR is required to promptly identify and document all deviations from the requirements of this specification. Deviation requests shall be reviewed and disposed by the PURCHASER prior to the performance of the related activity.

# 10.6	VENDOR shall guarantee that the equipment and material furnished shall be free of faults in design, workmanship and materials, and shall safely and satisfactorily meet the design and manufacturing requirement as shown in specification.

11.0	DRAWING AND DOCUMENTATION REQUIREMENT

11.1	VENDOR shall submit information and data with the proposal and after contract award in accordance with submittal schedule in sufficient detail to permit PURCHASER’s full understands and evaluation of the materials provided. VENDOR shall submit a complete drawing and document listed and drawing and document submittal schedule showing all drawings and documents to be submitted during the course of work and the dates of submittal and required return date by PURCHASER.

11.2	VENDOR shall submit the documents and drawings in accordance with “VENDOR DATA REQUIREMENTS” herein attached.

# ATTACHMENTS

Ⅰ	INSPECTION REQUIREMENTS

Ⅱ	VENDOR DATA REQUIREMENTS

Ⅲ	BILL OF QUANTITY

ATTACHMENT Ⅰ INSPECTION REQUIREMENTS

| NO. | Inspection Activities | Inspected by |  |
| --- | --- | --- | --- |
|  |  | VENDOR | PURCHASER |
| 1 2 3 4 5 6 | Quality Control Manual Inspection & Test Plan and Procedure Material Test Report / Material Certificate Test Report - Non-destructive examination - Hydrostatic test Check of Component Surface Defects, Dimension and Marking Final Shipping Inspection | H H W W W W | R R R R/W W R |

W : Witness inspection

R : Inspection report review

H : Holding inspection

ATTACHMENT Ⅱ VENDOR DATA REQUIREMENTS

| PROJECT : PURCHASER : |  |  | SHEET : 1 OF 1 SPEC. NO. : |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| GROUP NO. | DATA REQUIRED | QUOTE | APPROVAL |  | CERTIFIED |  |
|  |  | P | QUANTITY OF COPY | DUE DATE | QUANTITY OF COPY | DUE DATE |
| 1 2 3 4 6 7 8 | Deviation List, if any Dimensional Drawings Quality Control Manual Inspection procedure Test/Inspection Report Mill certificate Catalog | - 3 3 - - - | - 5 5 5 - - | - 2 weeks 2weeks 2weeks 2weeks - - | - 10 10 10 10 10 - | - 2 weeks 2 weeks 2 weeks 1 week After Test 1 week After Test - |
| GENERAL NOTE : - Data for “QUOTE” shall be submitted with quotation. - Data for “APPROVAL” shall be submitted within due date after commitment. - Data for “CERTIFIED” shall be submitted within due date after approval. - All certified documents shall be included in Final Vendor dossier. |  |  |  |  |  |  |

ATTACHMENT Ⅲ BILL OF QUANTITY

| ITEM | DESCRIPTION | SIZE | UNIT | TOTAL | REMARK |
| --- | --- | --- | --- | --- | --- |
| PIPE | HDPE SDR 11 | 160A | M | 12,745.0 |  |
|  | HDPE SDR 11 | 110A | M | 15,678.0 |  |
| 90° ELL | HDPE SDR 11 | 160A | EA | 4 |  |
|  | HDPE SDR 11 | 110A | EA | 29 |  |
| 45° ELL | HDPE SDR 11 | 160A | EA | 22 |  |
|  | HDPE SDR 11 | 110A | EA | 30 |  |
| TEE | HDPE SDR 11 | 110A | EA | 2 |  |
| CAP | HDPE SDR 11 | 160A | EA | 1 |  |
|  | HDPE SDR 11 | 110A | EA | 9 |  |
| EF SOCKET | HDPE SDR 11 | 160A | EA | 58 |  |
|  | HDPE SDR 11 | 110A | EA | 74 |  |
| TRANSMISSION FITTING | API 5L Gr.A / HDPE SDR 11 | 160A | EA | 1 |  |
|  | API 5L Gr.A / HDPE SDR 11 | 110A | EA | 7 |  |